DHWT Heat Pump Control Board

Simple Customer Operation Guide

Purpose The board controls the domestic hot water tank using the heat pump first. The electric heater is used as the second heating stage after the heat pump reaches its target. The LCD shows temperatures, EEV opening, setpoints, superheat, and fault messages.

# Normal Operating Sequence

When power is applied, all outputs are kept off and the EEV is driven fully closed.

The board reads the tank sensors and checks the safety inputs.

If the DHWT tank is cold, the water pump starts first.

After the pump pre-run time, the board checks the flow switch.

If flow is proven, the EEV opens to its starting position before the compressor starts.

The fan and compressor run to heat the tank to the heat pump setpoint.

When the top DHWT sensor reaches 50.0 C, the compressor stops and the EEV closes.

The pump and fan continue for the post-run time, then stop.

If the tank still needs higher temperature, the electric heater heats to 60.0 C.

When the top DHWT sensor reaches 60.0 C, the heater stops and the board waits.

# Temperature Targets

| Item | Customer meaning |
| --- | --- |
| Heat pump target | 50.0 C at the top DHWT sensor. |
| Heat pump restart | Starts again if the tank falls below the 50.0 C stage. Default hysteresis is 3.0 C. |
| Electric heater target | 60.0 C at the top DHWT sensor. |
| Electric heater restart | Starts when heater is enabled and the top tank temperature is about 3.0 C below the heater target. |
| Priority | If the tank falls below the heat pump stage, the compressor stage has priority over the electric heater. |

# EEV Behavior

At every board startup, the EEV is fully closed first to find its zero position.

Before compressor operation, the EEV opens to a safe starting position.

While the compressor is running, the board adjusts the EEV slowly using suction and evaporator temperature difference.

During running, the EEV is limited to a safe operating range and is not allowed to open fully.

When the compressor stops, when a fault occurs, or when the electric heater stage is active, the EEV closes to 0%.

# Fault And Reset Behavior

HP fault, LP fault, flow fault, sensor fault, freeze protection, high water temperature, or tank over-temperature will stop unsafe operation.

The board can automatically retry after a fault clears, up to 3 fault events.

If faults continue after the allowed retries, the board locks out for safety.

After lockout, the customer must remove the cause of the fault and reset or power-cycle the board.

The fault LED blinks while an active or latched fault is present.

The LCD stops rolling normal pages and shows the active fault message.

# LCD Messages

Normal pages roll about every 3 seconds.

Normal pages show suction and evaporator temperature, DHWT top and bottom temperature, EEV opening and DHWT setpoint, and superheat information.

During faults, the LCD shows messages such as HP Fault, LP Fault, FS Fault, sensor fault, high temperature fault, freeze fault, tank temperature fault, or EEV minimum opening fault.

# Customer Use Notes

Do not bypass HP, LP, flow switch, or sensor faults.

Make sure the pump and flow switch are working before compressor operation.

Make sure all temperature sensors are connected to the correct connectors.

If the board locks out after repeated faults, correct the fault first, then reset the board.

The electric heater must be wired through the correct relay output and protected by the proper external safety devices.

# Sensor Connectors

| Connector | Sensor |
| --- | --- |
| CN1 | Suction Temperature |
| CN2 | Evaporator Temperature |
| CN3 | Supply Hot Water Temperature |
| CN4 | Return Hot Water Temperature |
| CN5 | Outside Temperature |
| CN6 | Bottom DHWT Temperature |
| CN7 | Top DHWT Temperature |

# Quick Service Checklist

Confirm all seven temperature sensors are connected.

Confirm water pump operation and water flow.

Confirm HP and LP safety inputs are healthy.

Confirm the EEV cable and driver supply are connected.

Confirm the compressor and electric heater contactors are wired correctly.

Check LCD fault message before resetting a locked board.